## TS7.1a Automated sheet
TS7.1a Constant Pressure Test Method for Flexible Pipes
Date of Test | [5 empty] | Resource Consent/ TCC Contract No.
Development Name and Stage / TCC Contract Name
Project/ Pipe Location
Contractor Rep's Name | [5 empty] | Contractor's Company
Certifying Engineer's Name | [5 empty] | Engineer's Company
Council Witness Name | [5 empty] | Council
Test Establishment Information
Pipe No. | Pipe Material/ Type | PN rating |  | Length of Pipe Tested = L (km) | Pipe Nominal Diameter = DN (m) | Valid combination | Average Test Pressure = H (m) |  | Max. Test Pressure = 1.25xPNx100 = P (kPa)
1 |  |  | Note: 1bar = 10m = 100 kPa |  |  |  |  | Estimate or measure (To be supplied by the engineer prior to the test) |  | / /
2 | [9 empty] | / /
3 | [9 empty] | / /
4 | [9 empty] | / /
Pre-Test Checks |  |  |  | Yes / N/A (If N/A comment why) |  | Comment
Ensure pre-test preparation acceptable and air purged from line.
Ensure test section isolated and adequately supported against thrust.
Measured Volume of Make Up Water to Retain Test Pressure
|  | Time |  | Meter Reading (L) |  | Volume of Makeup Water (L)
Start Time
Meter readings shall be taken at 15min or 30min intervals. Test Duration Minimum = 2hrs Maximum = 5hrs | [7 empty] | Manual Calculation Space:
|  | Target Calculated Volumes Of Make Up Water |  | Measured Volume must be less than (L/15min) |  | Measured Volume must be less than (L/30min) |  | Measured Volume must be less than (L/hr)
Test Calculations
Calculated Allowable Make Up Water - Q (L/hr) | [5 empty] | Q=0.14*L*D*H
Test Results
Is the Measured Volume of Make Up Water less than the Calculated Allowable Make Up Volume? |  |  |  | (a) Y = Yes / N = No |  |  |  | To Pass (a) = Y
The thrust blocks are acceptably intact after test? |  |  |  | (b) Y = Thrust Blocks OK / N = Unacceptable |  |  |  | To Pass (b) = Y
There are no visible leaks? |  |  |  | (c) Y = No Leaks / N = Leaks were detected |  |  |  | To Pass (c) = Y
Overall Test Result:
Test Certification
I certify that this test was undertaken to the requirements of the Infrastructure Development Code
…………………………………………… |  |  | (Contractor's Representative) |  |  | …………………………... |  | (Certifying Engineer)
I certify that I was in attendance during the testing procedure acting as a witness for Tauranga City Council
…………………………………………… |  |  | (Council's Representative)
Notes
1. Before starting the test, all pre-test procedures outlined in IS-7.5 Pressure Testing checklist and NZS4404:2010 (Section C3.3) shall be completed. 2. Following the test measurement completion, all post test procedures outlined in IT-7.3.5 Post Test Procedure and NZS4404:2010 (Section C3.4) shall be completed. 3. Pressure logs shall be supplied to Council before full passing of test is recognised.

## TS7.1b Automated sheet
TS7.1b Constant Pressure Test Method for Visco-Elastic Pipes
Date of Test |  | Resource Consent/ TCC Contract No
Development Name and Stage/TCC Contract Name
Project/ Pipe Location
Contractor Rep's Name |  | Contractor's Company
Certifying Engineer's Name |  | Engineer's Company
Council Witness Name |  | Council
Test Establishment Information
Pipe Material/Type |  | Pressure Rating = PN (bar) |  | Note: 1bar = 10m = 100 kPa
Length of Pipe Tested = L (km) |  | Max. Test Pressure = 1.25xPNx100 = P (kPa)
Pipe Nominal Diameter = D (m) |  | Ave. Test Pressure = H (m) |  | Estimate or measure (to be supplied by the Engineer prior to test)
Pre-Test Checks |  | Yes / N/A (If N/A comment why) | Comment
Ensure pre-test preparation acceptable and air purged from line
Ensure test section isolated and adequately supported against thrust
Apply test pressure , shut off, allow to settle over 12hrs
Measured Volume of Make Up Water to Retain Test Pressure
| Time | Meter Reading (L) | Volume of Makeup Water (L)
Start
Reading at Hour 2
Reading at Hour 3 |  |  |  | (V1) = Makeup volume hour 2-3 (L)
Reading at Hour 4
Reading at Hour 5 |  |  |  | (V2) = Makeup volume hour 4-5 (L)
Test Calculations
Calculate Q (L/hr) Q=0.14*L*D*H |  | Allowable Make Up Volume (L/hr) 0.55*V1 + Q |  | (d)
Test Results
Is V2 < Allowable makeup volume (d)? |  | (a) Y = Yes / N = No |  | To Pass (a) = Y
The thrust blocks are acceptably intact after test? |  | (b)Y = Thrust Blocks OK / N = Unacceptable |  | To Pass (b) = Y
There are no visible leaks? |  | (c) Y = No Leaks / N = Leaks were detected |  | To Pass (c) = Y
Overall Test Result:
Test Certification
I certify that this test was undertaken to the requirements of the Infrastructure Development Code
…………………………... | (Contractor's Representative) |  | …………………………... | (Certifying Engineer)
I certify that I was in attendance during the testing procedure acting as a witness for Tauranga City Council
…………………………... | (Council's Representative)
Notes
1. Before starting the test, all pre-test procedures outlined in IS-7.5 Pressure Testing checklist and NZS4404:2010 (Section C3.3) shall be completed. 2. Following the test measurement completion, all post test procedures outlined in IT-7.3.5 Post Test Procedure and NZS4404:2010 (Section C3.4) shall be completed. 3. Pressure logs shall be supplied to Council before full passing of test is recognised

## TS7.1c Automated sheet
TS7.1c Pressure Rebound Test Method for Visco-Elastic Pipes
Date of Test |  |  |  |  | Resource Consent/ TCC Contract No.
Development Name and Stage/ TCC Contract Name
Project/Pipe Location
Contractor Rep's Name |  |  |  |  | Contractor's Company
Certifying Engineer's Name |  |  |  |  | Engineer's Company
Council Witness Name |  |  |  |  | Council
Test Establishment Information
Pipe No. | Pipe Material/ Type | PN rating Note: 1 bar = 10m = 100kPa | Length of Pipe Tested = L (m) | Pipe Nominal Diameter = DN (m) | Pipe Internal Diameter = D (m) | Pipe Wall Thickness = e (m) | Min Pressure Rating for all Pipes = PN (bar) | Max. Test Pressure = 1.25xPNx100 = P (kPa) | Concatenation
1 | [8 empty] | / / | / /
2 | [8 empty] | / / | / /
3 | [8 empty] | / / | / /
4 | [8 empty] | / / | / /
Pre-Test Checks |  |  | Yes / N/A (If N/A comment why) |  | Comment
Ensure pre-test preparation acceptable and air purged from line
Ensure test section isolated & adequately supported against thrust
Preliminary Phase Information
Raise pressure to test pressure (P) in less than 10 minutes - confirm test pressure |  | Hold pressure at (P) for 30 minutes then cease pumping and allow to decay for 60 minutes | Reading of remaining pressure after 60 mins (A) |  | Calculate 70% of test pressure (P) (B) |  | If value (A) > (B), continue. If value (A) < (B), test failed.
Air Volume Assessment
Quickly (less than 5mins) reduce pressure by 10-15% of the standard test pressure (P), measure volume of water bled out. |  | Initial Meter Reading | Final Meter Reading | Volume of Water Bled (litres) (ΔV) (Y) | Target Pressure Drop (ΔP)(kPa) | Recorded Pressure drop (kPa) (ΔP) | Temperature | Bulk Modulus of Water Ew
Air Volume Assessment | [5 empty] | MainTest phase
Pipe No. | Pipe material modulus Er | Calculate volume of water in pipe V=πx(D÷2)²xLx1000 (litres) | ΔV (Max Allowable Bled) = 1.2 x V x ΔP x ((1÷ Ew) + ((D ÷ e) ÷ Er)) (litres) | Sum ΔV (Max Allowable Bled) (X) (litres) | Decision If value (X) > (Y), continue. If value (X) < (Y), test failed. | Pressure readings | Time | Pressure (kPa) | concatenation
1 | [5 empty] | Pressure Rebound Start Time |  |  | /
2 | [5 empty] | Pressure at peak |  |  | /
3 | [5 empty] | Pressure after 30mins |  |  | /
4 | [5 empty] | Pressure after 90 mins |  |  | /
Test Results | [6 empty] | Overall Test Result:
Is "Main Test Phase" pressure rise acceptable i.e. gradual, levelling after about 30 minutes? |  |  | (a) Y = if the main test phase it a pass |  | To Pass (a) = Y
The thrust blocks are acceptably intact after test? |  |  | (b)Y = Thrust Blocks OK / N = Unacceptable |  | To Pass (b) = Y
There are no visible leaks? |  |  | (c) Y = No Leaks / N = Leaks were detected |  | To Pass (c) = Y
Test Certification
I certify that this test was undertaken to the requirements of the Infrastructure Development Code
…………………………………………… |  |  | (Contractor's Representative) |  | …………………………………………… |  |  | (Certifying Engineer)
I certify that I was in attendance during the testing procedure acting as a witness for Tauranga City Council
…………………………………………… |  |  | (Council's Representative)
Notes
1. Before starting the test, all pre-test procedures outlined in IS-7.5 Pressure Testing checklist and NZS4404:2010 (Section C3.3) shall be completed. 2. Following the test measurement completion, all post test procedures outlined in IT-7.3.5 Post Test Procedure and NZS4404:2010 (Section C3.4) shall be completed. 3. Pressure logs shall be supplied to Council before full passing of test is recognised

## TS7.1d Automated sheet
TS7.1d Visual Test Method
Date of Test |  | Resource Consent / TCC Contract No.
Development Name and Stage / TCC Contract Name
Project/ Pipe Location
Contractor Rep's Name |  | Contractor's Company
Certifying Engineer's Name |  | Engineer's Company
Council Witness Name |  | Council
Test Establishment Information
Pipe Material /Type |  | Pressure Rating = PN (bar) |  | Note: 1bar = 10m = 100 kPa
Length of Pipe Tested = L (km) |  | Max. Test Pressure = 1.25xPNx100 = P (kPa)
Pipe Nominal Diameter = D (m)
Pre-Test Checks |  | Yes / N/A (If N/A comment why) | Comment
Ensure pre-test preparation acceptable and air purged from line.
Ensure test section is isolated & adequately supported against thrust.
All non water utility epuipment is installed. i.e. Power service pillars, Fibre service leads, Gas, etc. are installed.
Meter manifolds and boxes are in place. End caps on and manifold is open.
PE Pipe Butt Weld. Weld bead is even on both sides of the weld and around the weld. Weld bead has no pitting. Pipe is "Round".
PE Pipe Electrofusion Welds. Weld coupler indicators have "Popped". No Plastic Malt has escaped from the weld zone. Pipe is "Round". Pipe alignment is true. Pipe has been Mechanically peeled.
PVC Pipe Witness marks have been inspected prior to backfilling.
Pipe trench is sufficiently backfilled to ensure pipe restraint.
All key operational fittings i.e. valves, fire hydrants, etc; lot connections, tees and bends are exposed, top and bottom.
Test Result
The thrust blocks are acceptably intact after test? |  | (a) Y = Thrust Blocks OK / N = Unacceptable |  | To Pass (a) = Y
There are no visible leaks? |  | (b) Y = No Leaks / N = Leaks were detected |  | To Pass (b) = Y
Overall Test Result:
Test Certification
I certify that this test was undertaken to the requirements of the Infrastructure Development Code
…………………………...……………… | (Contractor's Representative) |  | …………………………...……………… | (Certifying Engineer)
I certify that I was in attendance during the testing procedure acting as a witness for Tauranga City Council
…………………………...……………… | (Council's Representative)
Notes
1. Before starting the test, all pre-test procedures outlined in IS-7.5 Pressure Testing checklist and NZS4404:2010 (Section C3.3) shall be completed. 2. Following the test measurement completion, all post test procedures outlined in IT-7.3.5 Post Test Procedure and NZS4404:2010 (Section C3.4) shall be completed. 3. Pressure logs shall be supplied to Council before full passing of test is recognised.

## Manual tables (hidden)
TS7.1b Constant Pressure Test Method for Visco-Elastic Pipes
1. Before starting the test, all pre-test procedures outlined in NZS4404:2010 (Section C3.3) shall be completed
2. Following the test measurement completion, all post test procedures outlined in NZS4404:2010 (Section C3.4) shall be completed
3. Pressure logs shall be supplied to Council before full passing of test is recognised
TS7.1c Apx-A Polyethylene (PE) Pipe Dimensions | [11 empty] | Table 1 - Bulk Modulus of Water |  | Table 2 - Pipe Material Modulus - Er
|  |  | SDR17 |  | SDR13.6 |  | SDR11 |  | SDR9 |  |  |  |  | Temp °C | PE 80B | PE 100
PE80 |  |  | PN8 |  | PN10 |  | PN12.5 |  | PN16 |  |  | Temp °C | Bulk Modulus |  | 3hr | 3hr
PE100 |  |  | PN10 |  | PN12.5 |  | PN16 |  | PN20 |  |  | 5 | 2080000 | 5 | 680000 | 900000
DN | Min O.D (mm) | Max O.D (mm) | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. |  | 6 | 2086000 | 6 | 666000 | 876000
63 | 63 | 63.6 | - | - | - | - | 6.1 | 51.1 | - | - |  | 7 | 2092000 | 7 | 652000 | 862000
75 | 75 | 75.7 | 4.8 | 65.8 | 5.9 | 63.7 | 7.2 | 61 | 8.9 | 57.6 |  | 8 | 2098000 | 8 | 638000 | 848000
90 | 90 | 90.9 | 5.7 | 79 | 7 | 76.5 | 8.7 | 73.1 | 10.7 | 69.1 |  | 9 | 2104000 | 9 | 624000 | 834000
110 | 110 | 111 | 7 | 96.5 | 8.6 | 93.3 | 10.5 | 89.4 | 13 | 84.5 |  | 10 | 2110000 | 10 | 610000 | 820000
125 | 125 | 126.2 | 7.8 | 109.9 | 9.7 | 106.1 | 12 | 101.5 | 14.8 | 96 |  | 11 | 2116000 | 11 | 606000 | 806000
140 | 140 | 141.3 | 8.8 | 123.1 | 10.9 | 118.8 | 13.4 | 113.9 | 16.6 | 107.6 |  | 12 | 2122000 | 12 | 592000 | 792000
160 | 160 | 161.5 | 10 | 140.7 | 12.4 | 135.9 | 15.4 | 130 | 18.9 | 123.1 |  | 13 | 2128000 | 13 | 578000 | 778000
180 | 180 | 181.7 | 11.3 | 158.3 | 14 | 152.8 | 17.3 | 146.3 | 21.2 | 138.5 |  | 14 | 2134000 | 14 | 564000 | 764000
200 | 200 | 201.8 | 12.5 | 175.8 | 15.5 | 169.9 | 19.2 | 162.5 | 23.6 | 153.7 |  | 15 | 2140000 | 15 | 550000 | 750000
225 | 225 | 227.1 | 14.1 | 197.8 | 17.5 | 191.1 | 21.6 | 182.9 | 26.5 | 173.1 |  | 16 | 2146000 | 16 | 566000 | 736000
250 | 250 | 252.3 | 15.6 | 220 | 19.4 | 212.4 | 23.9 | 203.4 | 29.4 | 192.4 |  | 17 | 2152000 | 17 | 552000 | 722000
280 | 280 | 282.6 | 17.5 | 246.3 | 21.7 | 237.9 | 26.7 | 227.8 | 33 | 215.3 |  | 18 | 2158000 | 18 | 538000 | 708000
315 | 315 | 317.9 | 19.7 | 277.1 | 24.4 | 267.6 | 30.1 | 256.3 | 37.1 | 242.3 |  | 19 | 2164000 | 19 | 524000 | 694000
355 | 355 | 358.2 | 22.2 | 311.1 | 27.5 | 301.6 | 33.9 | 288.8 | 41.7 | 273.2 |  | 20 | 2170000 | 20 | 510000 | 680000
400 | 400 | 403.6 | 24.9 | 351.9 | 30.9 | 339.9 | 38.2 | 325.4 | 47 | 307.8 |  | 21 | 2178000 | 21 | 526000 | 686000
450 | 450 | 454.1 | 28.1 | 395.9 | 34.8 | 382.4 | 43 | 366.1 | 52.8 | 346.5 |  | 22 | 2186000 | 22 | 512000 | 672000
500 | 500 | 504.5 | 31.1 | 440 | 38.7 | 424.9 | 47.7 | 406.8 | 58.7 | 384.9 |  | 23 | 2194000 | 23 | 498000 | 658000
560 | 560 | 565 | 34.9 | 492.7 | 43.3 | 475.9 | 53.4 | 455.8 | 66.1 | 430.3 |  | 24 | 2202000 | 24 | 484000 | 644000
[12 empty] | 25 | 2210000 | 25 | 470000 | 630000
Note | [11 empty] | 26 | 2206000 | 26 | 486000 | 656000
• The information above is taken from "Civil Plastic Pipeline Systems" (Poliplex) by | [11 empty] | 27 | 2202000 | 27 | 472000 | 642000
Iplex Pipelines and is a guide only. | [11 empty] | 28 | 2198000 | 28 | 458000 | 628000
• All measurements are in millimetres (mm) | [11 empty] | 29 | 2194000 | 29 | 444000 | 614000
[12 empty] | 30 | 2230000 | 30 | 430000 | 600000
REBOUND READING WORK SHEET
| Pressure - manual check |  |  |  |  | Pressure - manual check |  |  |  |  | Pressure - continued as required
| min |  | kPa |  |  | min |  | kPa |  |  | min |  | kPa
| 1 |  |  |  |  | 21 |  |  |  |  | 41
| 2 |  |  |  |  | 22 |  |  |  |  | 42
| 3 |  |  |  |  | 23 |  |  |  |  | 43
| 4 |  |  |  |  | 24 |  |  |  |  | 44
| 5 |  |  |  |  | 25 |  |  |  |  | 45
| 6 |  |  |  |  | 26 |  |  |  |  | 46
| 7 |  |  |  |  | 27 |  |  |  |  | 47
| 8 |  |  |  |  | 28 |  |  |  |  | 48
| 9 |  |  |  |  | 29 |  |  |  |  | 49
| 10 |  |  |  |  | 30 |  |  |  |  | 50
| 11 |  |  |  |  | 31 |  |  |  |  | 51
| 12 |  |  |  |  | 32 |  |  |  |  | 52
| 13 |  |  |  |  | 33 |  |  |  |  | 53
| 14 |  |  |  |  | 34 |  |  |  |  | 54
| 15 |  |  |  |  | 35 |  |  |  |  | 55
| 16 |  |  |  |  | 36 |  |  |  |  | 56
| 17 |  |  |  |  | 37 |  |  |  |  | 57
| 18 |  |  |  |  | 38 |  |  |  |  | 58
| 19 |  |  |  |  | 39 |  |  |  |  | 59
| 20 |  |  |  |  | 40 |  |  |  |  | 60
Note: Sheet used to record pressure data at 1 minute increments, typically only the first 35mins are required.

## PE Pipe Dimensions (hidden)
TS7.1c Apx-A Polyethylene (PE) Pipe Dimensions
|  |  | SDR17 |  | SDR13.6 |  | SDR11 |  | SDR9
PN for PE80 |  |  | PN8 |  | PN10 |  | PN12.5 |  | PN16
PN for PE100 |  |  | PN10 |  | PN12.5 |  | PN16 |  | PN20
DN | Min O.D (mm) | Max O.D (mm) | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D.
63 | 63 | 63.6 | - | - | - | - | 6.1 | 51.1 | - | -
75 | 75 | 75.7 | 4.8 | 65.8 | 5.9 | 63.7 | 7.2 | 61 | 8.9 | 57.6
90 | 90 | 90.9 | 5.7 | 79 | 7 | 76.5 | 8.7 | 73.1 | 10.7 | 69.1
110 | 110 | 111 | 7 | 96.5 | 8.6 | 93.3 | 10.5 | 89.4 | 13 | 84.5
125 | 125 | 126.2 | 7.8 | 109.9 | 9.7 | 106.1 | 12 | 101.5 | 14.8 | 96
140 | 140 | 141.3 | 8.8 | 123.1 | 10.9 | 118.8 | 13.4 | 113.9 | 16.6 | 107.6
160 | 160 | 161.5 | 10 | 140.7 | 12.4 | 135.9 | 15.4 | 130 | 18.9 | 123.1
180 | 180 | 181.7 | 11.3 | 158.3 | 14 | 152.8 | 17.3 | 146.3 | 21.2 | 138.5
200 | 200 | 201.8 | 12.5 | 175.8 | 15.5 | 169.9 | 19.2 | 162.5 | 23.6 | 153.7
225 | 225 | 227.1 | 14.1 | 197.8 | 17.5 | 191.1 | 21.6 | 182.9 | 26.5 | 173.1
250 | 250 | 252.3 | 15.6 | 220 | 19.4 | 212.4 | 23.9 | 203.4 | 29.4 | 192.4
280 | 280 | 282.6 | 17.5 | 246.3 | 21.7 | 237.9 | 26.7 | 227.8 | 33 | 215.3
315 | 315 | 317.9 | 19.7 | 277.1 | 24.4 | 267.6 | 30.1 | 256.3 | 37.1 | 242.3
355 | 355 | 358.2 | 22.2 | 311.1 | 27.5 | 301.6 | 33.9 | 288.8 | 41.7 | 273.2
400 | 400 | 403.6 | 24.9 | 351.9 | 30.9 | 339.9 | 38.2 | 325.4 | 47 | 307.8
450 | 450 | 454.1 | 28.1 | 395.9 | 34.8 | 382.4 | 43 | 366.1 | 52.8 | 346.5
500 | 500 | 504.5 | 31.1 | 440 | 38.7 | 424.9 | 47.7 | 406.8 | 58.7 | 384.9
560 | 560 | 565 | 34.9 | 492.7 | 43.3 | 475.9 | 53.4 | 455.8 | 66.1 | 430.3
Note: | - The information above is taken from "Civil Plastic Pipeline Systems" (Poliplex) by Iplex Pipelines and is
a guide only.
- All measurements are in millimetres (mm)

## VlookupTables (hidden)
Table 1 - Bulk Modulus of Water - Ew |  | Table 2 - Pipe Material Modulus - Er |  |  |  | Material | PN | DN | Concatenation | Mean Wall | ID | Dropdown lists | pipe materal | PN No. | DN | ID | Pressure | Temp
Temperature | Bulk Modulus | Temperature |  |  |  | PE80B | PN8 | 0.063 | PE80B / PN8 / 0.063 | n/a | n/a
(°C) |  | (°C) | 3hr | Concatenation | 3hr | PE80B | PN8 | 0.075 | PE80B / PN8 / 0.075 | 0.0048 | 0.0658 |  | PE80B | PN8 | 0.063 | 0.0511 | 8 | 5
5 | 2080000 | 5 | PE80B | 5 / PE80B | 680000 | PE80B | PN8 | 0.09 | PE80B / PN8 / 0.09 | 0.0057 | 0.079 |  | PE100 | PN10 | 0.075 | 0.0576 | 10 | 6
6 | 2086000 | 6 | PE80B | 6 / PE80B | 666000 | PE80B | PN8 | 0.11 | PE80B / PN8 / 0.11 | 0.007 | 0.0965 |  |  | PN12.5 | 0.09 | 0.061 | 12.5 | 7
7 | 2092000 | 7 | PE80B | 7 / PE80B | 652000 | PE80B | PN8 | 0.125 | PE80B / PN8 / 0.125 | 0.0078 | 0.1099 |  |  | PN16 | 0.11 | 0.0637 | 16 | 8
8 | 2098000 | 8 | PE80B | 8 / PE80B | 638000 | PE80B | PN8 | 0.14 | PE80B / PN8 / 0.14 | 0.0088 | 0.1231 |  |  | PN20 | 0.125 | 0.0658 | 20 | 9
9 | 2104000 | 9 | PE80B | 9 / PE80B | 624000 | PE80B | PN8 | 0.16 | PE80B / PN8 / 0.16 | 0.01 | 0.1407 |  |  |  | 0.14 | 0.0691 |  | 10
10 | 2110000 | 10 | PE80B | 10 / PE80B | 610000 | PE80B | PN8 | 0.18 | PE80B / PN8 / 0.18 | 0.0113 | 0.1583 |  |  |  | 0.16 | 0.0731 |  | 11
11 | 2116000 | 11 | PE80B | 11 / PE80B | 606000 | PE80B | PN8 | 0.2 | PE80B / PN8 / 0.2 | 0.0125 | 0.1758 |  |  |  | 0.18 | 0.0765 |  | 12
12 | 2122000 | 12 | PE80B | 12 / PE80B | 592000 | PE80B | PN8 | 0.225 | PE80B / PN8 / 0.225 | 0.0141 | 0.1978 |  |  |  | 0.2 | 0.079 |  | 13
13 | 2128000 | 13 | PE80B | 13 / PE80B | 578000 | PE80B | PN8 | 0.25 | PE80B / PN8 / 0.25 | 0.0156 | 0.22 |  | Y |  | 0.225 | 0.0845 |  | 14
14 | 2134000 | 14 | PE80B | 14 / PE80B | 564000 | PE80B | PN8 | 0.28 | PE80B / PN8 / 0.28 | 0.0175 | 0.2463 |  | N |  | 0.25 | 0.0894 |  | 15
15 | 2140000 | 15 | PE80B | 15 / PE80B | 550000 | PE80B | PN8 | 0.315 | PE80B / PN8 / 0.315 | 0.0197 | 0.2771 |  |  |  | 0.28 | 0.0933 |  | 16
16 | 2146000 | 16 | PE80B | 16 / PE80B | 566000 | PE80B | PN8 | 0.355 | PE80B / PN8 / 0.355 | 0.0222 | 0.3111 |  |  |  | 0.315 | 0.096 |  | 17
17 | 2152000 | 17 | PE80B | 17 / PE80B | 552000 | PE80B | PN8 | 0.4 | PE80B / PN8 / 0.4 | 0.0249 | 0.3519 |  |  |  | 0.355 | 0.0965 |  | 18
18 | 2158000 | 18 | PE80B | 18 / PE80B | 538000 | PE80B | PN8 | 0.45 | PE80B / PN8 / 0.45 | 0.0281 | 0.3959 |  |  |  | 0.4 | 0.1015 |  | 19
19 | 2164000 | 19 | PE80B | 19 / PE80B | 524000 | PE80B | PN8 | 0.5 | PE80B / PN8 / 0.5 | 0.0311 | 0.44 |  |  |  | 0.45 | 0.1061 |  | 20
20 | 2170000 | 20 | PE80B | 20 / PE80B | 510000 | PE80B | PN8 | 0.56 | PE80B / PN8 / 0.56 | 0.0349 | 0.4927 |  |  |  | 0.5 | 0.1076 |  | 21
21 | 2178000 | 21 | PE80B | 21 / PE80B | 526000 | PE80B | PN10 | 0.063 | PE80B / PN10 / 0.063 | n/a | n/a |  |  |  | 0.56 | 0.1099 |  | 22
22 | 2186000 | 22 | PE80B | 22 / PE80B | 512000 | PE80B | PN10 | 0.075 | PE80B / PN10 / 0.075 | 0.0059 | 0.0637 |  |  |  |  | 0.1139 |  | 23
23 | 2194000 | 23 | PE80B | 23 / PE80B | 498000 | PE80B | PN10 | 0.09 | PE80B / PN10 / 0.09 | 0.007 | 0.0765 |  |  |  |  | 0.1188 |  | 24
24 | 2202000 | 24 | PE80B | 24 / PE80B | 484000 | PE80B | PN10 | 0.11 | PE80B / PN10 / 0.11 | 0.0086 | 0.0933 |  |  |  |  | 0.1231 |  | 25
25 | 2210000 | 25 | PE80B | 25 / PE80B | 470000 | PE80B | PN10 | 0.125 | PE80B / PN10 / 0.125 | 0.0097 | 0.1061 |  |  |  |  | 0.13 |  | 26
26 | 2206000 | 26 | PE80B | 26 / PE80B | 486000 | PE80B | PN10 | 0.14 | PE80B / PN10 / 0.14 | 0.0109 | 0.1188 |  |  |  |  | 0.1359 |  | 27
27 | 2202000 | 27 | PE80B | 27 / PE80B | 472000 | PE80B | PN10 | 0.16 | PE80B / PN10 / 0.16 | 0.0124 | 0.1359 |  |  |  |  | 0.1385 |  | 28
28 | 2198000 | 28 | PE80B | 28 / PE80B | 458000 | PE80B | PN10 | 0.18 | PE80B / PN10 / 0.18 | 0.014 | 0.1528 |  |  |  |  | 0.1407 |  | 29
29 | 2194000 | 29 | PE80B | 29 / PE80B | 444000 | PE80B | PN10 | 0.2 | PE80B / PN10 / 0.2 | 0.0155 | 0.1699 |  |  |  |  | 0.1463 |  | 30
30 | 2230000 | 30 | PE80B | 30 / PE80B | 430000 | PE80B | PN10 | 0.225 | PE80B / PN10 / 0.225 | 0.0175 | 0.1911 |  |  |  |  | 0.1528
|  | 5 | PE100 | 5 / PE100 | 900000 | PE80B | PN10 | 0.25 | PE80B / PN10 / 0.25 | 0.0194 | 0.2124 |  |  |  |  | 0.1537
|  | 6 | PE100 | 6 / PE100 | 876000 | PE80B | PN10 | 0.28 | PE80B / PN10 / 0.28 | 0.0217 | 0.2379 |  |  |  |  | 0.1583
|  | 7 | PE100 | 7 / PE100 | 862000 | PE80B | PN10 | 0.315 | PE80B / PN10 / 0.315 | 0.0244 | 0.2676 |  |  |  |  | 0.1625
|  | 8 | PE100 | 8 / PE100 | 848000 | PE80B | PN10 | 0.355 | PE80B / PN10 / 0.355 | 0.0275 | 0.3016 |  |  |  |  | 0.1699
|  | 9 | PE100 | 9 / PE100 | 834000 | PE80B | PN10 | 0.4 | PE80B / PN10 / 0.4 | 0.0309 | 0.3399 |  |  |  |  | 0.1731
|  | 10 | PE100 | 10 / PE100 | 820000 | PE80B | PN10 | 0.45 | PE80B / PN10 / 0.45 | 0.0348 | 0.3824 |  |  |  |  | 0.1758
|  | 11 | PE100 | 11 / PE100 | 806000 | PE80B | PN10 | 0.5 | PE80B / PN10 / 0.5 | 0.0387 | 0.4249 |  |  |  |  | 0.1829
|  | 12 | PE100 | 12 / PE100 | 792000 | PE80B | PN10 | 0.56 | PE80B / PN10 / 0.56 | 0.0433 | 0.4759 |  |  |  |  | 0.1911
|  | 13 | PE100 | 13 / PE100 | 778000 | PE80B | PN12.5 | 0.063 | PE80B / PN12.5 / 0.063 | 0.0061 | 0.0511 |  |  |  |  | 0.1924
|  | 14 | PE100 | 14 / PE100 | 764000 | PE80B | PN12.5 | 0.075 | PE80B / PN12.5 / 0.075 | 0.0072 | 0.061 |  |  |  |  | 0.1978
|  | 15 | PE100 | 15 / PE100 | 750000 | PE80B | PN12.5 | 0.09 | PE80B / PN12.5 / 0.09 | 0.0087 | 0.0731 |  |  |  |  | 0.2034
|  | 16 | PE100 | 16 / PE100 | 736000 | PE80B | PN12.5 | 0.11 | PE80B / PN12.5 / 0.11 | 0.0105 | 0.0894 |  |  |  |  | 0.2124
|  | 17 | PE100 | 17 / PE100 | 722000 | PE80B | PN12.5 | 0.125 | PE80B / PN12.5 / 0.125 | 0.012 | 0.1015 |  |  |  |  | 0.2153
|  | 18 | PE100 | 18 / PE100 | 708000 | PE80B | PN12.5 | 0.14 | PE80B / PN12.5 / 0.14 | 0.0134 | 0.1139 |  |  |  |  | 0.22
|  | 19 | PE100 | 19 / PE100 | 694000 | PE80B | PN12.5 | 0.16 | PE80B / PN12.5 / 0.16 | 0.0154 | 0.13 |  |  |  |  | 0.2278
|  | 20 | PE100 | 20 / PE100 | 680000 | PE80B | PN12.5 | 0.18 | PE80B / PN12.5 / 0.18 | 0.0173 | 0.1463 |  |  |  |  | 0.2379
|  | 21 | PE100 | 21 / PE100 | 686000 | PE80B | PN12.5 | 0.2 | PE80B / PN12.5 / 0.2 | 0.0192 | 0.1625 |  |  |  |  | 0.2423
|  | 22 | PE100 | 22 / PE100 | 672000 | PE80B | PN12.5 | 0.225 | PE80B / PN12.5 / 0.225 | 0.0216 | 0.1829 |  |  |  |  | 0.2463
|  | 23 | PE100 | 23 / PE100 | 658000 | PE80B | PN12.5 | 0.25 | PE80B / PN12.5 / 0.25 | 0.0239 | 0.2034 |  |  |  |  | 0.2563
|  | 24 | PE100 | 24 / PE100 | 644000 | PE80B | PN12.5 | 0.28 | PE80B / PN12.5 / 0.28 | 0.0267 | 0.2278 |  |  |  |  | 0.2676
|  | 25 | PE100 | 25 / PE100 | 630000 | PE80B | PN12.5 | 0.315 | PE80B / PN12.5 / 0.315 | 0.0301 | 0.2563 |  |  |  |  | 0.2732
|  | 26 | PE100 | 26 / PE100 | 656000 | PE80B | PN12.5 | 0.355 | PE80B / PN12.5 / 0.355 | 0.0339 | 0.2888 |  |  |  |  | 0.2771
|  | 27 | PE100 | 27 / PE100 | 642000 | PE80B | PN12.5 | 0.4 | PE80B / PN12.5 / 0.4 | 0.0382 | 0.3254 |  |  |  |  | 0.2888
|  | 28 | PE100 | 28 / PE100 | 628000 | PE80B | PN12.5 | 0.45 | PE80B / PN12.5 / 0.45 | 0.043 | 0.3661 |  |  |  |  | 0.3016
|  | 29 | PE100 | 29 / PE100 | 614000 | PE80B | PN12.5 | 0.5 | PE80B / PN12.5 / 0.5 | 0.0477 | 0.4068 |  |  |  |  | 0.3078
|  | 30 | PE100 | 30 / PE100 | 600000 | PE80B | PN12.5 | 0.56 | PE80B / PN12.5 / 0.56 | 0.0534 | 0.4558 |  |  |  |  | 0.3111
[6 empty] | PE80B | PN16 | 0.063 | PE80B / PN16 / 0.063 | n/a | n/a |  |  |  |  | 0.3254
[6 empty] | PE80B | PN16 | 0.075 | PE80B / PN16 / 0.075 | 0.0089 | 0.0576 |  |  |  |  | 0.3399
[6 empty] | PE80B | PN16 | 0.09 | PE80B / PN16 / 0.09 | 0.0107 | 0.0691 |  |  |  |  | 0.3465
[6 empty] | PE80B | PN16 | 0.11 | PE80B / PN16 / 0.11 | 0.013 | 0.0845 |  |  |  |  | 0.3519
[6 empty] | PE80B | PN16 | 0.125 | PE80B / PN16 / 0.125 | 0.0148 | 0.096 |  |  |  |  | 0.3661
[6 empty] | PE80B | PN16 | 0.14 | PE80B / PN16 / 0.14 | 0.0166 | 0.1076 |  |  |  |  | 0.3824
[6 empty] | PE80B | PN16 | 0.16 | PE80B / PN16 / 0.16 | 0.0189 | 0.1231 |  |  |  |  | 0.3849
[6 empty] | PE80B | PN16 | 0.18 | PE80B / PN16 / 0.18 | 0.0212 | 0.1385 |  |  |  |  | 0.3959
[6 empty] | PE80B | PN16 | 0.2 | PE80B / PN16 / 0.2 | 0.0236 | 0.1537 |  |  |  |  | 0.4068
[6 empty] | PE80B | PN16 | 0.225 | PE80B / PN16 / 0.225 | 0.0265 | 0.1731 |  |  |  |  | 0.4249
[6 empty] | PE80B | PN16 | 0.25 | PE80B / PN16 / 0.25 | 0.0294 | 0.1924 |  |  |  |  | 0.4303
[6 empty] | PE80B | PN16 | 0.28 | PE80B / PN16 / 0.28 | 0.033 | 0.2153 |  |  |  |  | 0.44
[6 empty] | PE80B | PN16 | 0.315 | PE80B / PN16 / 0.315 | 0.0371 | 0.2423 |  |  |  |  | 0.4558
[6 empty] | PE80B | PN16 | 0.355 | PE80B / PN16 / 0.355 | 0.0417 | 0.2732 |  |  |  |  | 0.4759
[6 empty] | PE80B | PN16 | 0.4 | PE80B / PN16 / 0.4 | 0.047 | 0.3078 |  |  |  |  | 0.4927
[6 empty] | PE80B | PN16 | 0.45 | PE80B / PN16 / 0.45 | 0.0528 | 0.3465
[6 empty] | PE80B | PN16 | 0.5 | PE80B / PN16 / 0.5 | 0.0587 | 0.3849
[6 empty] | PE80B | PN16 | 0.56 | PE80B / PN16 / 0.56 | 0.0661 | 0.4303
[6 empty] | PE100 | PN10 | 0.063 | PE100 / PN10 / 0.063 | n/a | n/a
[6 empty] | PE100 | PN10 | 0.075 | PE100 / PN10 / 0.075 | 0.0048 | 0.0658
[6 empty] | PE100 | PN10 | 0.09 | PE100 / PN10 / 0.09 | 0.0057 | 0.079
[6 empty] | PE100 | PN10 | 0.11 | PE100 / PN10 / 0.11 | 0.007 | 0.0965
[6 empty] | PE100 | PN10 | 0.125 | PE100 / PN10 / 0.125 | 0.0078 | 0.1099
[6 empty] | PE100 | PN10 | 0.14 | PE100 / PN10 / 0.14 | 0.0088 | 0.1231
[6 empty] | PE100 | PN10 | 0.16 | PE100 / PN10 / 0.16 | 0.01 | 0.1407
[6 empty] | PE100 | PN10 | 0.18 | PE100 / PN10 / 0.18 | 0.0113 | 0.1583
[6 empty] | PE100 | PN10 | 0.2 | PE100 / PN10 / 0.2 | 0.0125 | 0.1758
[6 empty] | PE100 | PN10 | 0.225 | PE100 / PN10 / 0.225 | 0.0141 | 0.1978
[6 empty] | PE100 | PN10 | 0.25 | PE100 / PN10 / 0.25 | 0.0156 | 0.22
[6 empty] | PE100 | PN10 | 0.28 | PE100 / PN10 / 0.28 | 0.0175 | 0.2463
[6 empty] | PE100 | PN10 | 0.315 | PE100 / PN10 / 0.315 | 0.0197 | 0.2771
[6 empty] | PE100 | PN10 | 0.355 | PE100 / PN10 / 0.355 | 0.0222 | 0.3111
[6 empty] | PE100 | PN10 | 0.4 | PE100 / PN10 / 0.4 | 0.0249 | 0.3519
[6 empty] | PE100 | PN10 | 0.45 | PE100 / PN10 / 0.45 | 0.0281 | 0.3959
[6 empty] | PE100 | PN10 | 0.5 | PE100 / PN10 / 0.5 | 0.0311 | 0.44
[6 empty] | PE100 | PN10 | 0.56 | PE100 / PN10 / 0.56 | 0.0349 | 0.4927
[6 empty] | PE100 | PN12.5 | 0.063 | PE100 / PN12.5 / 0.063 | n/a | n/a
[6 empty] | PE100 | PN12.5 | 0.075 | PE100 / PN12.5 / 0.075 | 0.0059 | 0.0637
[6 empty] | PE100 | PN12.5 | 0.09 | PE100 / PN12.5 / 0.09 | 0.007 | 0.0765
[6 empty] | PE100 | PN12.5 | 0.11 | PE100 / PN12.5 / 0.11 | 0.0086 | 0.0933
[6 empty] | PE100 | PN12.5 | 0.125 | PE100 / PN12.5 / 0.125 | 0.0097 | 0.1061
[6 empty] | PE100 | PN12.5 | 0.14 | PE100 / PN12.5 / 0.14 | 0.0109 | 0.1188
[6 empty] | PE100 | PN12.5 | 0.16 | PE100 / PN12.5 / 0.16 | 0.0124 | 0.1359
[6 empty] | PE100 | PN12.5 | 0.18 | PE100 / PN12.5 / 0.18 | 0.014 | 0.1528
[6 empty] | PE100 | PN12.5 | 0.2 | PE100 / PN12.5 / 0.2 | 0.0155 | 0.1699
[6 empty] | PE100 | PN12.5 | 0.225 | PE100 / PN12.5 / 0.225 | 0.0175 | 0.1911
[6 empty] | PE100 | PN12.5 | 0.25 | PE100 / PN12.5 / 0.25 | 0.0194 | 0.2124
[6 empty] | PE100 | PN12.5 | 0.28 | PE100 / PN12.5 / 0.28 | 0.0217 | 0.2379
[6 empty] | PE100 | PN12.5 | 0.315 | PE100 / PN12.5 / 0.315 | 0.0244 | 0.2676
[6 empty] | PE100 | PN12.5 | 0.355 | PE100 / PN12.5 / 0.355 | 0.0275 | 0.3016
[6 empty] | PE100 | PN12.5 | 0.4 | PE100 / PN12.5 / 0.4 | 0.0309 | 0.3399
[6 empty] | PE100 | PN12.5 | 0.45 | PE100 / PN12.5 / 0.45 | 0.0348 | 0.3824
[6 empty] | PE100 | PN12.5 | 0.5 | PE100 / PN12.5 / 0.5 | 0.0387 | 0.4249
[6 empty] | PE100 | PN12.5 | 0.56 | PE100 / PN12.5 / 0.56 | 0.0433 | 0.4759
[6 empty] | PE100 | PN16 | 0.063 | PE100 / PN16 / 0.063 | 0.0061 | 0.0511
[6 empty] | PE100 | PN16 | 0.075 | PE100 / PN16 / 0.075 | 0.0072 | 0.061
[6 empty] | PE100 | PN16 | 0.09 | PE100 / PN16 / 0.09 | 0.0087 | 0.0731
[6 empty] | PE100 | PN16 | 0.11 | PE100 / PN16 / 0.11 | 0.0105 | 0.0894
[6 empty] | PE100 | PN16 | 0.125 | PE100 / PN16 / 0.125 | 0.012 | 0.1015
[6 empty] | PE100 | PN16 | 0.14 | PE100 / PN16 / 0.14 | 0.0134 | 0.1139
[6 empty] | PE100 | PN16 | 0.16 | PE100 / PN16 / 0.16 | 0.0154 | 0.13
[6 empty] | PE100 | PN16 | 0.18 | PE100 / PN16 / 0.18 | 0.0173 | 0.1463
[6 empty] | PE100 | PN16 | 0.2 | PE100 / PN16 / 0.2 | 0.0192 | 0.1625
[6 empty] | PE100 | PN16 | 0.225 | PE100 / PN16 / 0.225 | 0.0216 | 0.1829
[6 empty] | PE100 | PN16 | 0.25 | PE100 / PN16 / 0.25 | 0.0239 | 0.2034
[6 empty] | PE100 | PN16 | 0.28 | PE100 / PN16 / 0.28 | 0.0267 | 0.2278
[6 empty] | PE100 | PN16 | 0.315 | PE100 / PN16 / 0.315 | 0.0301 | 0.2563
[6 empty] | PE100 | PN16 | 0.355 | PE100 / PN16 / 0.355 | 0.0339 | 0.2888
[6 empty] | PE100 | PN16 | 0.4 | PE100 / PN16 / 0.4 | 0.0382 | 0.3254
[6 empty] | PE100 | PN16 | 0.45 | PE100 / PN16 / 0.45 | 0.043 | 0.3661
[6 empty] | PE100 | PN16 | 0.5 | PE100 / PN16 / 0.5 | 0.0477 | 0.4068
[6 empty] | PE100 | PN16 | 0.56 | PE100 / PN16 / 0.56 | 0.0534 | 0.4558
[6 empty] | PE100 | PN20 | 0.063 | PE100 / PN20 / 0.063 | n/a | n/a
[6 empty] | PE100 | PN20 | 0.075 | PE100 / PN20 / 0.075 | 0.0089 | 0.0576
[6 empty] | PE100 | PN20 | 0.09 | PE100 / PN20 / 0.09 | 0.0107 | 0.0691
[6 empty] | PE100 | PN20 | 0.11 | PE100 / PN20 / 0.11 | 0.013 | 0.0845
[6 empty] | PE100 | PN20 | 0.125 | PE100 / PN20 / 0.125 | 0.0148 | 0.096
[6 empty] | PE100 | PN20 | 0.14 | PE100 / PN20 / 0.14 | 0.0166 | 0.1076
[6 empty] | PE100 | PN20 | 0.16 | PE100 / PN20 / 0.16 | 0.0189 | 0.1231
[6 empty] | PE100 | PN20 | 0.18 | PE100 / PN20 / 0.18 | 0.0212 | 0.1385
[6 empty] | PE100 | PN20 | 0.2 | PE100 / PN20 / 0.2 | 0.0236 | 0.1537
[6 empty] | PE100 | PN20 | 0.225 | PE100 / PN20 / 0.225 | 0.0265 | 0.1731
[6 empty] | PE100 | PN20 | 0.25 | PE100 / PN20 / 0.25 | 0.0294 | 0.1924
[6 empty] | PE100 | PN20 | 0.28 | PE100 / PN20 / 0.28 | 0.033 | 0.2153
[6 empty] | PE100 | PN20 | 0.315 | PE100 / PN20 / 0.315 | 0.0371 | 0.2423
[6 empty] | PE100 | PN20 | 0.355 | PE100 / PN20 / 0.355 | 0.0417 | 0.2732
[6 empty] | PE100 | PN20 | 0.4 | PE100 / PN20 / 0.4 | 0.047 | 0.3078
[6 empty] | PE100 | PN20 | 0.45 | PE100 / PN20 / 0.45 | 0.0528 | 0.3465
[6 empty] | PE100 | PN20 | 0.5 | PE100 / PN20 / 0.5 | 0.0587 | 0.3849
[6 empty] | PE100 | PN20 | 0.56 | PE100 / PN20 / 0.56 | 0.0661 | 0.4303

## PVC Pipe Dimensions (hidden)
[12 empty] | Note: | http://www.iplex.com.au/iplex.php?page=lib&lib=12&sec=78 | . | Series | Material | PN | DN | Concatenation | Mean Wall | ID
PVC-U | [12 empty] | All measurements are in millimetres (mm) | . |  | UPVC | PN6 | 15 | / UPVC / PN6 / 15 | n/a | n/a
UPVC |  | PN6 |  | PN8 |  | PN12 |  | PN15 |  | PN18 |  |  | . T = mean wall thickness | . |  | UPVC | PN6 | 20 | / UPVC / PN6 / 20 | n/a | n/a
DN | O.D (mm) | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. |  | . ID = mean inside diameter | . |  | UPVC | PN6 | 25 | / UPVC / PN6 / 25 | n/a | n/a
15 |  | - | - | - | - | 1.5 | 18.3 | 1.5 | 18.3 | 1.8 | 17.8 |  |  | . |  | UPVC | PN6 | 32 | / UPVC / PN6 / 32 | n/a | n/a
20 | 26.75 | - | - | - | - | 1.5 | 23.7 | 1.5 | 23.7 | 2.2 | 22.4 |  |  | . |  | UPVC | PN6 | 40 | / UPVC / PN6 / 40 | 1.5 | 45.2
25 | 33.55 | - | - | 1.5 | 30.5 | 1.9 | 29.8 | 1.9 | 29.8 | 2.7 | 28.1 |  |  | . |  | UPVC | PN6 | 50 | / UPVC / PN6 / 50 | 1.8 | 56.8
32 | 42.25 | - | - | 1.9 | 38.5 | 2.4 | 37.5 | 2.4 | 37.5 | 3.4 | 35.4 |  |  | . |  | UPVC | PN6 | 65 | / UPVC / PN6 / 65 | 2.2 | 71
40 | 48.25 | 1.5 | 45.2 | 2.1 | 44.1 | 2.7 | 42.8 | 2.7 | 42.8 | 3.9 | 40.5 |  |  | . |  | UPVC | PN6 | 80 | / UPVC / PN6 / 80 | 2.6 | 83.7
50 | 60.35 | 1.8 | 56.8 | 2.6 | 55.2 | 3.3 | 53.7 | 3.3 | 53.7 | 4.9 | 50.5 |  |  | . |  | UPVC | PN6 | 100 | / UPVC / PN6 / 100 | 3.2 | 107.8
65 | 75.35 | 2.2 | 71 | 3.2 | 68.9 | 4.2 | 67 | 4.2 | 67 | 6.1 | 63.2 |  |  | . |  | UPVC | PN6 | 125 | / UPVC / PN6 / 125 | 4 | 132.2
80 | 88.9 | 2.6 | 83.7 | 3.8 | 81.3 | 4.9 | 79 | 4.9 | 79 | 7.1 | 74.6 |  |  | . |  | UPVC | PN6 | 150 | / UPVC / PN6 / 150 | 4.5 | 151.3
100 | 114.3 | 3.2 | 107.8 | 4.8 | 104.6 | 6.3 | 101.7 | 6.3 | 101.7 | 9.1 | 96 |  |  | . |  | UPVC | PN6 | 200 | / UPVC / PN6 / 200 | 5.7 | 213.8
125 | 140.2 | 4 | 132.2 | 5.9 | 128.4 | 7.6 | 124.9 | 7.6 | 124.9 | - | - |  |  | . |  | UPVC | PN6 | 225 | / UPVC / PN6 / 225 | 6.3 | 237.7
150 | 160.3 | 4.5 | 151.3 | 6.7 | 146.9 | 8.8 | 142.7 | 8.8 | 142.7 | 12.8 | 134.7 |  |  | . |  | UPVC | PN6 | 250 | / UPVC / PN6 / 250 | 7.1 | 266.2
200 | 225.3 | 5.7 | 213.8 | 8.4 | 208.5 | 11.1 | 203.1 | 11.1 | 203.1 | 16.2 | 192.9 |  |  | . |  | UPVC | PN6 | 300 | / UPVC / PN6 / 300 | 8 | 299.5
225 | 250.4 | 6.3 | 237.7 | 9.3 | 231.7 | 12.3 | 225.8 | 12.3 | 225.8 | 18 | 214.4 |  |  | . |  | UPVC | PN6 | 375 | / UPVC / PN6 / 375 | 10.1 | 380.3
250 | 280.4 | 7.1 | 266.2 | 10.5 | 259.4 | 13.7 | 252.9 | 13.7 | 252.9 | 20.1 | 239.9 |  |  | . |  | UPVC | PN8 | 15 | / UPVC / PN8 / 15 | n/a | n/a
300 | 315.5 | 8 | 299.5 | 11.7 | 292 | 15.5 | 284.5 | 15.5 | 284.5 | 22.6 | 270.2 |  |  | . |  | UPVC | PN8 | 20 | / UPVC / PN8 / 20 | n/a | n/a
375 | 400.5 | 10.1 | 380.3 | 14.9 | 370.7 | 19.6 | 363.3 | 19.6 | 363.3 | - | - |  |  | . |  | UPVC | PN8 | 25 | / UPVC / PN8 / 25 | 1.5 | 30.5
[14 empty] | . |  | UPVC | PN8 | 32 | / UPVC / PN8 / 32 | 1.9 | 38.5
Series 1 - White | [13 empty] | . |  | UPVC | PN8 | 40 | / UPVC / PN8 / 40 | 2.1 | 44.1
PVC-M | [12 empty] | http://www.iplex.com.au/iplex.php?page=lib&lib=25&sec=165 | . |  | UPVC | PN8 | 50 | / UPVC / PN8 / 50 | 2.6 | 55.2
MPVC |  | PN6 |  | PN9 |  | PN12 |  | PN15 |  | PN18 |  |  |  | . |  | UPVC | PN8 | 65 | / UPVC / PN8 / 65 | 3.2 | 68.9
DN | O.D (mm) | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. |  |  | . |  | UPVC | PN8 | 80 | / UPVC / PN8 / 80 | 3.8 | 81.3
100 | 114.3 | 3.2 | 108.7 | 3.2 | 108 | 4.1 | 106.1 | 5.1 | 104.2 | 6 | 102.3 |  |  | . |  | UPVC | PN8 | 100 | / UPVC / PN8 / 100 | 4.8 | 104.6
150 | 160.3 | 3.7 | 152.9 | 4.3 | 151.7 | 5.7 | 148.9 | 7.1 | 146.2 | 8.3 | 143.7 |  |  | . |  | UPVC | PN8 | 125 | / UPVC / PN8 / 125 | 5.9 | 128.4
200 | 225.3 | 5.2 | 215 | 6.1 | 213.1 | 8 | 209.3 | 9.9 | 205.5 | 11.7 | 202 |  |  | . |  | UPVC | PN8 | 150 | / UPVC / PN8 / 150 | 6.7 | 146.9
225 | 250.4 | 5.8 | 238.8 | 6.7 | 237 | 8.8 | 232.8 | 10.9 | 228.6 | 13.1 | 224.3 |  |  | . |  | UPVC | PN8 | 200 | / UPVC / PN8 / 200 | 8.4 | 208.5
250 | 280.4 | 6.4 | 267.6 | 7.5 | 265.5 | 9.9 | 260.6 | 12.4 | 255.6 | 14.5 | 251.4 |  |  | . |  | UPVC | PN8 | 225 | / UPVC / PN8 / 225 | 9.3 | 231.7
300 | 315.5 | 7.2 | 301.1 | 8.4 | 298.7 | 11.2 | 293.2 | 13.8 | 288 | 16.3 | 282.9 |  |  | . |  | UPVC | PN8 | 250 | / UPVC / PN8 / 250 | 10.5 | 259.4
375 | 400.5 | 9.2 | 382.1 | 10.6 | 379.3 | 14.1 | 372.3 | 17.5 | 365.6 | 20.7 | 359.1 |  |  | . |  | UPVC | PN8 | 300 | / UPVC / PN8 / 300 | 11.7 | 292
450 | 500.5 | 11.8 | 476.9 | 13.8 | 472.9 | 18.1 | 464.3 | - | - | - | - |  |  | . |  | UPVC | PN8 | 375 | / UPVC / PN8 / 375 | 14.9 | 370.7
500 | 560.5 | 13.2 | 534.1 | 15.5 | 529.6 | 20.3 | 520 | - | - | - | - |  |  | . |  | UPVC | PN12 | 15 | / UPVC / PN12 / 15 | 1.5 | 18.3
575 | 630.5 | 14.7 | 601.1 | 17.3 | 596 | 22.8 | 585 | - | - | - | - |  |  | . |  | UPVC | PN12 | 20 | / UPVC / PN12 / 20 | 1.5 | 23.7
[14 empty] | . |  | UPVC | PN12 | 25 | / UPVC / PN12 / 25 | 1.9 | 29.8
[14 empty] | . |  | UPVC | PN12 | 32 | / UPVC / PN12 / 32 | 2.4 | 37.5
Series 2 - Blue | [13 empty] | . |  | UPVC | PN12 | 40 | / UPVC / PN12 / 40 | 2.7 | 42.8
PVC-M | [12 empty] | http://www.iplex.com.au/iplex.php?page=lib&lib=25&sec=165 | . |  | UPVC | PN12 | 50 | / UPVC / PN12 / 50 | 3.3 | 53.7
MPVC |  | PN9 |  | PN12 |  | PN15 |  | PN18 |  | PN20 |  |  |  | . |  | UPVC | PN12 | 65 | / UPVC / PN12 / 65 | 4.2 | 67
DN | O.D (mm) | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. |  |  | . |  | UPVC | PN12 | 80 | / UPVC / PN12 / 80 | 4.9 | 79
100 | 121.9 | - | - | 4.4 | 113.1 | 5.7 | 110.3 | 6.4 | 109.1 | 7.1 | 107.8 |  |  | . |  | UPVC | PN12 | 100 | / UPVC / PN12 / 100 | 6.3 | 101.7
150 | 177.4 | - | - | 6.3 | 164.8 | 8.3 | 160.8 | 9.2 | 159 | 10.2 | 157 |  |  | . |  | UPVC | PN12 | 125 | / UPVC / PN12 / 125 | 7.6 | 124.9
200 | 232.3 | - | - | 8.2 | 215.9 | 10.8 | 210.7 | 12 | 208.3 | 13.3 | 205.8 |  |  | . |  | UPVC | PN12 | 150 | / UPVC / PN12 / 150 | 8.8 | 142.7
225 | 259.3 | 7 | 245.4 | 9.2 | 241 | 12 | 235.1 | 13.4 | 232.5 | 14.8 | 229.7 |  |  | . |  | UPVC | PN12 | 200 | / UPVC / PN12 / 200 | 11.1 | 203.1
250 | 286.2 | 7.7 | 270.9 | 10.1 | 266 | 13.3 | 259.7 | 14.8 | 256.6 | 16.4 | 253.4 |  |  | . |  | UPVC | PN12 | 225 | / UPVC / PN12 / 225 | 12.3 | 225.8
300 | 345.4 | 9.3 | 326.9 | 12.2 | 321 | 16 | 313.5 | 17.8 | 309.8 | 19.7 | 306.1 |  |  | . |  | UPVC | PN12 | 250 | / UPVC / PN12 / 250 | 13.7 | 252.9
375 | 426.2 | 11.4 | 403.5 | 14.9 | 396.4 | 19.7 | 386.9 | 22 | 382.2 | 24.3 | 377.7 |  |  | . |  | UPVC | PN12 | 300 | / UPVC / PN12 / 300 | 15.5 | 284.5
450 | 507 | 13.5 | 480.1 | 17.8 | 471.5 | 23.4 | 460.2 | - | - | - | - |  |  | . |  | UPVC | PN12 | 375 | / UPVC / PN12 / 375 | 19.6 | 363.3
500 | 560.3 | 15.5 | 529.3 | 20.3 | 519.8 | - | - | - | - | - | - |  |  | . |  | UPVC | PN15 | 15 | / UPVC / PN15 / 15 | 1.5 | 18.3
[14 empty] | . |  | UPVC | PN15 | 20 | / UPVC / PN15 / 20 | 1.5 | 23.7
[14 empty] | . | Series 1 | MPVC | PN6 | 100 | Series 1 / MPVC / PN6 / 100 | 3.2 | 108.7 | UPVC | PN15 | 25 | UPVC / PN15 / 25 | 1.9 | 29.8
PVC-O | [12 empty] | http://molecor.com/en/pvc-o-pipes/range-pvc-o-tomr-pipes | . | Series 1 | MPVC | PN6 | 150 | Series 1 / MPVC / PN6 / 150 | 3.7 | 152.9 | UPVC | PN15 | 32 | UPVC / PN15 / 32 | 2.4 | 37.5
PVC-O |  | PN12.5 |  | PN16 |  | PN20 |  | PN25 | [5 empty] | . | Series 1 | MPVC | PN6 | 200 | Series 1 / MPVC / PN6 / 200 | 5.2 | 215 | UPVC | PN15 | 40 | UPVC / PN15 / 40 | 2.7 | 42.8
DN | O.D (mm) | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. | Mean Wall | Mean I.D. |  |  |  |  | . | Series 1 | MPVC | PN6 | 225 | Series 1 / MPVC / PN6 / 225 | 5.8 | 238.8 | UPVC | PN15 | 50 | UPVC / PN15 / 50 | 3.3 | 53.7
90 | 90.15 | - | - | 2 | 84 | 2.5 | 84 | 3.1 | 82.2 |  |  |  |  | . | Series 1 | MPVC | PN6 | 250 | Series 1 / MPVC / PN6 / 250 | 6.4 | 267.6 | UPVC | PN15 | 65 | UPVC / PN15 / 65 | 4.2 | 67
110 | 110.2 | 2.2 | 104.4 | 2.4 | 104 | 3.1 | 103.2 | 3.8 | 101.4 |  |  |  |  | . | Series 1 | MPVC | PN6 | 300 | Series 1 / MPVC / PN6 / 300 | 7.2 | 301.1 | UPVC | PN15 | 80 | UPVC / PN15 / 80 | 4.9 | 79
125 | 125.2 | 2.5 | 118.8 | 2.8 | 117.8 | 3.5 | 117 | 4.3 | 115.2 |  |  |  |  | . | Series 1 | MPVC | PN6 | 375 | Series 1 / MPVC / PN6 / 375 | 9.2 | 382.1 | UPVC | PN15 | 100 | UPVC / PN15 / 100 | 6.3 | 101.7
140 | 140.25 | 2.8 | 133 | 3.1 | 132.4 | 3.9 | 131.2 | 4.8 | 129.2 |  |  |  |  | . | Series 1 | MPVC | PN6 | 450 | Series 1 / MPVC / PN6 / 450 | 11.8 | 476.9 | UPVC | PN15 | 125 | UPVC / PN15 / 125 | 7.6 | 124.9
160 | 160.25 | 3.2 | 152 | 3.5 | 151.4 | 4.4 | 150 | 5.5 | 147.6 |  |  |  |  | . | Series 1 | MPVC | PN6 | 500 | Series 1 / MPVC / PN6 / 500 | 13.2 | 534.1 | UPVC | PN15 | 150 | UPVC / PN15 / 150 | 8.8 | 142.7
200 | 200.3 | 4 | 190 | 4.4 | 189.2 | 5.5 | 187.4 | 6.9 | 184.4 |  |  |  |  | . | Series 1 | MPVC | PN6 | 575 | Series 1 / MPVC / PN6 / 575 | 14.7 | 601.1 | UPVC | PN15 | 200 | UPVC / PN15 / 200 | 11.1 | 203.1
225 | 225.35 | 4.5 | 213.6 | 5 | 212.8 | 6.2 | 210.8 | 7.7 | 207.4 |  |  |  |  | . | Series 1 | MPVC | PN9 | 100 | Series 1 / MPVC / PN9 / 100 | 3.2 | 108 | UPVC | PN15 | 225 | UPVC / PN15 / 225 | 12.3 | 225.8
250 | 250.4 | 5 | 237.4 | 5.5 | 236.4 | 6.9 | 234.2 | 8.6 | 230.6 |  |  |  |  | . | Series 1 | MPVC | PN9 | 150 | Series 1 / MPVC / PN9 / 150 | 4.3 | 151.7 | UPVC | PN15 | 250 | UPVC / PN15 / 250 | 13.7 | 252.9
315 | 315.5 | 6.3 | 299.2 | 6.9 | 298 | 8.7 | 295.2 | 10.8 | 290.6 |  |  |  |  | . | Series 1 | MPVC | PN9 | 200 | Series 1 / MPVC / PN9 / 200 | 6.1 | 213.1 | UPVC | PN15 | 300 | UPVC / PN15 / 300 | 15.5 | 284.5
355 | 355.55 | 7.1 | 337.4 | 7.8 | 336 | 9.8 | 332.4 | 12.2 | 327.2 |  |  |  |  | . | Series 1 | MPVC | PN9 | 225 | Series 1 / MPVC / PN9 / 225 | 6.7 | 237 | UPVC | PN15 | 375 | UPVC / PN15 / 375 | 19.6 | 363.3
400 | 400.6 | 8 | 379.8 | 8.8 | 378.4 | 11 | 374.8 | 13.7 | 369 |  |  |  |  | . | Series 1 | MPVC | PN9 | 250 | Series 1 / MPVC / PN9 / 250 | 7.5 | 265.5 | UPVC | PN18 | 15 | UPVC / PN18 / 15 | 1.8 | 17.8
450 | 450.7 | 8.9 | 427.6 | 9.9 | 426 | 12.4 | 421.4 | 15.4 | 415 |  |  |  |  | . | Series 1 | MPVC | PN9 | 300 | Series 1 / MPVC / PN9 / 300 | 8.4 | 298.7 | UPVC | PN18 | 20 | UPVC / PN18 / 20 | 2.2 | 22.4
500 | 500.75 | 9.9 | 474.6 | 11 | 472.8 | 13.7 | 468.6 | 17.1 | 461.2 |  |  |  |  | . | Series 1 | MPVC | PN9 | 375 | Series 1 / MPVC / PN9 / 375 | 10.6 | 379.3 | UPVC | PN18 | 25 | UPVC / PN18 / 25 | 2.7 | 28.1
630 | 630.95 | 12.6 | 597.8 | 13.8 | 595.8 | 17.3 | 590.4 | 21.6 | 581 |  |  |  |  | . | Series 1 | MPVC | PN9 | 450 | Series 1 / MPVC / PN9 / 450 | 13.8 | 472.9 | UPVC | PN18 | 32 | UPVC / PN18 / 32 | 3.4 | 35.4
710 | 710.5 | 14.2 | 674.8 | 15.4 | 671.4 | 19.2 | 665.6 | 24.4 | 654.6 |  |  |  |  | . | Series 1 | MPVC | PN9 | 500 | Series 1 / MPVC / PN9 / 500 | 15.5 | 529.6 | UPVC | PN18 | 40 | UPVC / PN18 / 40 | 3.9 | 40.5
800 | 801 | 16.3 | 760.4 | 17.4 | 757.8 | 21.6 | 750.4 | - | - |  |  |  |  | . | Series 1 | MPVC | PN9 | 575 | Series 1 / MPVC / PN9 / 575 | 17.3 | 596 | UPVC | PN18 | 50 | UPVC / PN18 / 50 | 4.9 | 50.5
[15 empty] | Series 1 | MPVC | PN12 | 100 | Series 1 / MPVC / PN12 / 100 | 4.1 | 106.1 | UPVC | PN18 | 65 | UPVC / PN18 / 65 | 6.1 | 63.2
[15 empty] | Series 1 | MPVC | PN12 | 150 | Series 1 / MPVC / PN12 / 150 | 5.7 | 148.9 | UPVC | PN18 | 80 | UPVC / PN18 / 80 | 7.1 | 74.6
[15 empty] | Series 1 | MPVC | PN12 | 200 | Series 1 / MPVC / PN12 / 200 | 8 | 209.3 | UPVC | PN18 | 100 | UPVC / PN18 / 100 | 9.1 | 96
[15 empty] | Series 1 | MPVC | PN12 | 225 | Series 1 / MPVC / PN12 / 225 | 8.8 | 232.8 | UPVC | PN18 | 125 | UPVC / PN18 / 125 | - | -
[15 empty] | Series 1 | MPVC | PN12 | 250 | Series 1 / MPVC / PN12 / 250 | 9.9 | 260.6 | UPVC | PN18 | 150 | UPVC / PN18 / 150 | 12.8 | 134.7
[15 empty] | Series 1 | MPVC | PN12 | 300 | Series 1 / MPVC / PN12 / 300 | 11.2 | 293.2 | UPVC | PN18 | 200 | UPVC / PN18 / 200 | 16.2 | 192.9
[15 empty] | Series 1 | MPVC | PN12 | 375 | Series 1 / MPVC / PN12 / 375 | 14.1 | 372.3 | UPVC | PN18 | 225 | UPVC / PN18 / 225 | 18 | 214.4
[15 empty] | Series 1 | MPVC | PN12 | 450 | Series 1 / MPVC / PN12 / 450 | 18.1 | 464.3 | UPVC | PN18 | 250 | UPVC / PN18 / 250 | 20.1 | 239.9
[15 empty] | Series 1 | MPVC | PN12 | 500 | Series 1 / MPVC / PN12 / 500 | 20.3 | 520 | UPVC | PN18 | 300 | UPVC / PN18 / 300 | 22.6 | 270.2
[15 empty] | Series 1 | MPVC | PN12 | 575 | Series 1 / MPVC / PN12 / 575 | 22.8 | 585 | UPVC | PN18 | 375 | UPVC / PN18 / 375 | - | -
[15 empty] | Series 1 | MPVC | PN15 | 100 | Series 1 / MPVC / PN15 / 100 | 5.1 | 104.2
[15 empty] | Series 1 | MPVC | PN15 | 150 | Series 1 / MPVC / PN15 / 150 | 7.1 | 146.2
[15 empty] | Series 1 | MPVC | PN15 | 200 | Series 1 / MPVC / PN15 / 200 | 9.9 | 205.5
[15 empty] | Series 1 | MPVC | PN15 | 225 | Series 1 / MPVC / PN15 / 225 | 10.9 | 228.6
[15 empty] | Series 1 | MPVC | PN15 | 250 | Series 1 / MPVC / PN15 / 250 | 12.4 | 255.6
[15 empty] | Series 1 | MPVC | PN15 | 300 | Series 1 / MPVC / PN15 / 300 | 13.8 | 288
[15 empty] | Series 1 | MPVC | PN15 | 375 | Series 1 / MPVC / PN15 / 375 | 17.5 | 365.6
[15 empty] | Series 1 | MPVC | PN15 | 450 | Series 1 / MPVC / PN15 / 450 | - | -
[15 empty] | Series 1 | MPVC | PN15 | 500 | Series 1 / MPVC / PN15 / 500 | - | -
[15 empty] | Series 1 | MPVC | PN15 | 575 | Series 1 / MPVC / PN15 / 575 | - | -
[15 empty] | Series 1 | MPVC | PN18 | 100 | Series 1 / MPVC / PN18 / 100 | 6 | 102.3
[15 empty] | Series 1 | MPVC | PN18 | 150 | Series 1 / MPVC / PN18 / 150 | 8.3 | 143.7
[15 empty] | Series 1 | MPVC | PN18 | 200 | Series 1 / MPVC / PN18 / 200 | 11.7 | 202
[15 empty] | Series 1 | MPVC | PN18 | 225 | Series 1 / MPVC / PN18 / 225 | 13.1 | 224.3
[15 empty] | Series 1 | MPVC | PN18 | 250 | Series 1 / MPVC / PN18 / 250 | 14.5 | 251.4
[15 empty] | Series 1 | MPVC | PN18 | 300 | Series 1 / MPVC / PN18 / 300 | 16.3 | 282.9
[15 empty] | Series 1 | MPVC | PN18 | 375 | Series 1 / MPVC / PN18 / 375 | 20.7 | 359.1
[15 empty] | Series 1 | MPVC | PN18 | 450 | Series 1 / MPVC / PN18 / 450 | - | -
[15 empty] | Series 1 | MPVC | PN18 | 500 | Series 1 / MPVC / PN18 / 500 | - | -
[15 empty] | Series 1 | MPVC | PN18 | 575 | Series 1 / MPVC / PN18 / 575 | - | -
[15 empty] | Series 2 | MPVC | PN9 | 100 | Series 2 / MPVC / PN9 / 100 | - | -
[15 empty] | Series 2 | MPVC | PN9 | 150 | Series 2 / MPVC / PN9 / 150 | - | -
[15 empty] | Series 2 | MPVC | PN9 | 200 | Series 2 / MPVC / PN9 / 200 | - | -
[15 empty] | Series 2 | MPVC | PN9 | 225 | Series 2 / MPVC / PN9 / 225 | 7 | 245.4
[15 empty] | Series 2 | MPVC | PN9 | 250 | Series 2 / MPVC / PN9 / 250 | 7.7 | 270.9
[15 empty] | Series 2 | MPVC | PN9 | 300 | Series 2 / MPVC / PN9 / 300 | 9.3 | 326.9
[15 empty] | Series 2 | MPVC | PN9 | 375 | Series 2 / MPVC / PN9 / 375 | 11.4 | 403.5
[15 empty] | Series 2 | MPVC | PN9 | 450 | Series 2 / MPVC / PN9 / 450 | 13.5 | 480.1
[15 empty] | Series 2 | MPVC | PN9 | 500 | Series 2 / MPVC / PN9 / 500 | 15.5 | 529.3
[15 empty] | Series 2 | MPVC | PN12 | 100 | Series 2 / MPVC / PN12 / 100 | 4.4 | 113.1
[15 empty] | Series 2 | MPVC | PN12 | 150 | Series 2 / MPVC / PN12 / 150 | 6.3 | 164.8
[15 empty] | Series 2 | MPVC | PN12 | 200 | Series 2 / MPVC / PN12 / 200 | 8.2 | 215.9
[15 empty] | Series 2 | MPVC | PN12 | 225 | Series 2 / MPVC / PN12 / 225 | 9.2 | 241
[15 empty] | Series 2 | MPVC | PN12 | 250 | Series 2 / MPVC / PN12 / 250 | 10.1 | 266
[15 empty] | Series 2 | MPVC | PN12 | 300 | Series 2 / MPVC / PN12 / 300 | 12.2 | 321
[15 empty] | Series 2 | MPVC | PN12 | 375 | Series 2 / MPVC / PN12 / 375 | 14.9 | 396.4
[15 empty] | Series 2 | MPVC | PN12 | 450 | Series 2 / MPVC / PN12 / 450 | 17.8 | 471.5
[15 empty] | Series 2 | MPVC | PN12 | 500 | Series 2 / MPVC / PN12 / 500 | 20.3 | 519.8
[15 empty] | Series 2 | MPVC | PN15 | 100 | Series 2 / MPVC / PN15 / 100 | 5.7 | 110.3
[15 empty] | Series 2 | MPVC | PN15 | 150 | Series 2 / MPVC / PN15 / 150 | 8.3 | 160.8
[15 empty] | Series 2 | MPVC | PN15 | 200 | Series 2 / MPVC / PN15 / 200 | 10.8 | 210.7
[15 empty] | Series 2 | MPVC | PN15 | 225 | Series 2 / MPVC / PN15 / 225 | 12 | 235.1
[15 empty] | Series 2 | MPVC | PN15 | 250 | Series 2 / MPVC / PN15 / 250 | 13.3 | 259.7
[15 empty] | Series 2 | MPVC | PN15 | 300 | Series 2 / MPVC / PN15 / 300 | 16 | 313.5
[15 empty] | Series 2 | MPVC | PN15 | 375 | Series 2 / MPVC / PN15 / 375 | 19.7 | 386.9
[15 empty] | Series 2 | MPVC | PN15 | 450 | Series 2 / MPVC / PN15 / 450 | 23.4 | 460.2
[15 empty] | Series 2 | MPVC | PN15 | 500 | Series 2 / MPVC / PN15 / 500 | - | -
[15 empty] | Series 2 | MPVC | PN18 | 100 | Series 2 / MPVC / PN18 / 100 | 6.4 | 109.1
[15 empty] | Series 2 | MPVC | PN18 | 150 | Series 2 / MPVC / PN18 / 150 | 9.2 | 159
[15 empty] | Series 2 | MPVC | PN18 | 200 | Series 2 / MPVC / PN18 / 200 | 12 | 208.3
[15 empty] | Series 2 | MPVC | PN18 | 225 | Series 2 / MPVC / PN18 / 225 | 13.4 | 232.5
[15 empty] | Series 2 | MPVC | PN18 | 250 | Series 2 / MPVC / PN18 / 250 | 14.8 | 256.6
[15 empty] | Series 2 | MPVC | PN18 | 300 | Series 2 / MPVC / PN18 / 300 | 17.8 | 309.8
[15 empty] | Series 2 | MPVC | PN18 | 375 | Series 2 / MPVC / PN18 / 375 | 22 | 382.2
[15 empty] | Series 2 | MPVC | PN18 | 450 | Series 2 / MPVC / PN18 / 450 | - | -
[15 empty] | Series 2 | MPVC | PN18 | 500 | Series 2 / MPVC / PN18 / 500 | - | -
[15 empty] | Series 2 | MPVC | PN20 | 100 | Series 2 / MPVC / PN20 / 100 | 7.1 | 107.8
[15 empty] | Series 2 | MPVC | PN20 | 150 | Series 2 / MPVC / PN20 / 150 | 10.2 | 157
[15 empty] | Series 2 | MPVC | PN20 | 200 | Series 2 / MPVC / PN20 / 200 | 13.3 | 205.8
[15 empty] | Series 2 | MPVC | PN20 | 225 | Series 2 / MPVC / PN20 / 225 | 14.8 | 229.7
[15 empty] | Series 2 | MPVC | PN20 | 250 | Series 2 / MPVC / PN20 / 250 | 16.4 | 253.4
[15 empty] | Series 2 | MPVC | PN20 | 300 | Series 2 / MPVC / PN20 / 300 | 19.7 | 306.1
[15 empty] | Series 2 | MPVC | PN20 | 375 | Series 2 / MPVC / PN20 / 375 | 24.3 | 377.7
[15 empty] | Series 2 | MPVC | PN20 | 450 | Series 2 / MPVC / PN20 / 450 | - | -
[15 empty] | Series 2 | MPVC | PN20 | 500 | Series 2 / MPVC / PN20 / 500 | - | -
[16 empty] | PVC-O | PN12.5 | 90 | / PVC-O / PN12.5 / 90 | - | -
[16 empty] | PVC-O | PN12.5 | 110 | / PVC-O / PN12.5 / 110 | 2.2 | 104.4
[16 empty] | PVC-O | PN12.5 | 125 | / PVC-O / PN12.5 / 125 | 2.5 | 118.8
[16 empty] | PVC-O | PN12.5 | 140 | / PVC-O / PN12.5 / 140 | 2.8 | 133
[16 empty] | PVC-O | PN12.5 | 160 | / PVC-O / PN12.5 / 160 | 3.2 | 152
[16 empty] | PVC-O | PN12.5 | 200 | / PVC-O / PN12.5 / 200 | 4 | 190
[16 empty] | PVC-O | PN12.5 | 225 | / PVC-O / PN12.5 / 225 | 4.5 | 213.6
[16 empty] | PVC-O | PN12.5 | 250 | / PVC-O / PN12.5 / 250 | 5 | 237.4
[16 empty] | PVC-O | PN12.5 | 315 | / PVC-O / PN12.5 / 315 | 6.3 | 299.2
[16 empty] | PVC-O | PN12.5 | 355 | / PVC-O / PN12.5 / 355 | 7.1 | 337.4
[16 empty] | PVC-O | PN12.5 | 400 | / PVC-O / PN12.5 / 400 | 8 | 379.8
[16 empty] | PVC-O | PN12.5 | 450 | / PVC-O / PN12.5 / 450 | 8.9 | 427.6
[16 empty] | PVC-O | PN12.5 | 500 | / PVC-O / PN12.5 / 500 | 9.9 | 474.6
[16 empty] | PVC-O | PN12.5 | 630 | / PVC-O / PN12.5 / 630 | 12.6 | 597.8
[16 empty] | PVC-O | PN12.5 | 710 | / PVC-O / PN12.5 / 710 | 14.2 | 674.8
[16 empty] | PVC-O | PN12.5 | 800 | / PVC-O / PN12.5 / 800 | 16.3 | 760.4
[16 empty] | PVC-O | PN16 | 90 | / PVC-O / PN16 / 90 | 2 | 84
[16 empty] | PVC-O | PN16 | 110 | / PVC-O / PN16 / 110 | 2.4 | 104
[16 empty] | PVC-O | PN16 | 125 | / PVC-O / PN16 / 125 | 2.8 | 117.8
[16 empty] | PVC-O | PN16 | 140 | / PVC-O / PN16 / 140 | 3.1 | 132.4
[16 empty] | PVC-O | PN16 | 160 | / PVC-O / PN16 / 160 | 3.5 | 151.4
[16 empty] | PVC-O | PN16 | 200 | / PVC-O / PN16 / 200 | 4.4 | 189.2
[16 empty] | PVC-O | PN16 | 225 | / PVC-O / PN16 / 225 | 5 | 212.8
[16 empty] | PVC-O | PN16 | 250 | / PVC-O / PN16 / 250 | 5.5 | 236.4
[16 empty] | PVC-O | PN16 | 315 | / PVC-O / PN16 / 315 | 6.9 | 298
[16 empty] | PVC-O | PN16 | 355 | / PVC-O / PN16 / 355 | 7.8 | 336
[16 empty] | PVC-O | PN16 | 400 | / PVC-O / PN16 / 400 | 8.8 | 378.4
[16 empty] | PVC-O | PN16 | 450 | / PVC-O / PN16 / 450 | 9.9 | 426
[16 empty] | PVC-O | PN16 | 500 | / PVC-O / PN16 / 500 | 11 | 472.8
[16 empty] | PVC-O | PN16 | 630 | / PVC-O / PN16 / 630 | 13.8 | 595.8
[16 empty] | PVC-O | PN16 | 710 | / PVC-O / PN16 / 710 | 15.4 | 671.4
[16 empty] | PVC-O | PN16 | 800 | / PVC-O / PN16 / 800 | 17.4 | 757.8
[16 empty] | PVC-O | PN20 | 90 | / PVC-O / PN20 / 90 | 2.5 | 84
[16 empty] | PVC-O | PN20 | 110 | / PVC-O / PN20 / 110 | 3.1 | 103.2
[16 empty] | PVC-O | PN20 | 125 | / PVC-O / PN20 / 125 | 3.5 | 117
[16 empty] | PVC-O | PN20 | 140 | / PVC-O / PN20 / 140 | 3.9 | 131.2
[16 empty] | PVC-O | PN20 | 160 | / PVC-O / PN20 / 160 | 4.4 | 150
[16 empty] | PVC-O | PN20 | 200 | / PVC-O / PN20 / 200 | 5.5 | 187.4
[16 empty] | PVC-O | PN20 | 225 | / PVC-O / PN20 / 225 | 6.2 | 210.8
[16 empty] | PVC-O | PN20 | 250 | / PVC-O / PN20 / 250 | 6.9 | 234.2
[16 empty] | PVC-O | PN20 | 315 | / PVC-O / PN20 / 315 | 8.7 | 295.2
[16 empty] | PVC-O | PN20 | 355 | / PVC-O / PN20 / 355 | 9.8 | 332.4
[16 empty] | PVC-O | PN20 | 400 | / PVC-O / PN20 / 400 | 11 | 374.8
[16 empty] | PVC-O | PN20 | 450 | / PVC-O / PN20 / 450 | 12.4 | 421.4
[16 empty] | PVC-O | PN20 | 500 | / PVC-O / PN20 / 500 | 13.7 | 468.6
[16 empty] | PVC-O | PN20 | 630 | / PVC-O / PN20 / 630 | 17.3 | 590.4
[16 empty] | PVC-O | PN20 | 710 | / PVC-O / PN20 / 710 | 19.2 | 665.6
[16 empty] | PVC-O | PN20 | 800 | / PVC-O / PN20 / 800 | 21.6 | 750.4
[16 empty] | PVC-O | PN25 | 90 | / PVC-O / PN25 / 90 | 3.1 | 82.2
[16 empty] | PVC-O | PN25 | 110 | / PVC-O / PN25 / 110 | 3.8 | 101.4
[16 empty] | PVC-O | PN25 | 125 | / PVC-O / PN25 / 125 | 4.3 | 115.2
[16 empty] | PVC-O | PN25 | 140 | / PVC-O / PN25 / 140 | 4.8 | 129.2
[16 empty] | PVC-O | PN25 | 160 | / PVC-O / PN25 / 160 | 5.5 | 147.6
[16 empty] | PVC-O | PN25 | 200 | / PVC-O / PN25 / 200 | 6.9 | 184.4
[16 empty] | PVC-O | PN25 | 225 | / PVC-O / PN25 / 225 | 7.7 | 207.4
[16 empty] | PVC-O | PN25 | 250 | / PVC-O / PN25 / 250 | 8.6 | 230.6
[16 empty] | PVC-O | PN25 | 315 | / PVC-O / PN25 / 315 | 10.8 | 290.6
[16 empty] | PVC-O | PN25 | 355 | / PVC-O / PN25 / 355 | 12.2 | 327.2
[16 empty] | PVC-O | PN25 | 400 | / PVC-O / PN25 / 400 | 13.7 | 369
[16 empty] | PVC-O | PN25 | 450 | / PVC-O / PN25 / 450 | 15.4 | 415
[16 empty] | PVC-O | PN25 | 500 | / PVC-O / PN25 / 500 | 17.1 | 461.2
[16 empty] | PVC-O | PN25 | 630 | / PVC-O / PN25 / 630 | 21.6 | 581
[16 empty] | PVC-O | PN25 | 710 | / PVC-O / PN25 / 710 | 24.4 | 654.6
[16 empty] | PVC-O | PN25 | 800 | / PVC-O / PN25 / 800 | - | -

## Table for sheet a (hidden)
Material | PN | DN (mm) | DN (m)
UPVC | PN8 | 100 | 0.1
UPVC | PN8 | 150 | 0.15
UPVC | PN8 | 200 | 0.2
UPVC | PN8 | 250 | 0.25
UPVC | PN8 | 300 | 0.3
UPVC | PN8 | 375 | 0.375
UPVC | PN9 | 100 | 0.1
UPVC | PN9 | 150 | 0.15
UPVC | PN9 | 200 | 0.2
UPVC | PN9 | 250 | 0.25
UPVC | PN9 | 300 | 0.3
UPVC | PN9 | 375 | 0.375
UPVC | PN12 | 100 | 0.1
UPVC | PN12 | 150 | 0.15
UPVC | PN12 | 200 | 0.2
UPVC | PN12 | 250 | 0.25
UPVC | PN12 | 300 | 0.3
UPVC | PN12 | 375 | 0.375
MPVC | PN9 | 100 | 0.1
MPVC | PN9 | 150 | 0.15
MPVC | PN9 | 200 | 0.2
MPVC | PN9 | 250 | 0.25
MPVC | PN9 | 300 | 0.3
MPVC | PN9 | 375 | 0.375
MPVC | PN12 | 100 | 0.1
MPVC | PN12 | 150 | 0.15
MPVC | PN12 | 200 | 0.2
MPVC | PN12 | 250 | 0.25
MPVC | PN12 | 300 | 0.3
MPVC | PN12 | 375 | 0.375
MPVC | PN15 | 100 | 0.1
MPVC | PN15 | 150 | 0.15
MPVC | PN15 | 200 | 0.2
MPVC | PN15 | 250 | 0.25
MPVC | PN15 | 300 | 0.3
MPVC | PN15 | 375 | 0.375

## VlookupTablePVC (hidden)
Material | PN | DN (m) | DN | Concatenation | Mean Wall | ID | Valid combination |  |  | Dropdown lists | Material | PN | DN | ID | Pressure
UPVC | PN8 | 100 | 0.1 | UPVC / PN8 / 0.1 | 4.8 | 104.6 | Yes
UPVC | PN8 | 150 | 0.15 | UPVC / PN8 / 0.15 | 6.7 | 146.9 | Yes |  | Yes | Yes | MPVC | PN8 | 0.1 | 0.0183 | 6
UPVC | PN8 | 200 | 0.2 | UPVC / PN8 / 0.2 | 8.4 | 208.5 | Yes |  | n/a | No | UPVC | PN9 | 0.15 | 0.0237 | 8
UPVC | PN8 | 250 | 0.25 | UPVC / PN8 / 0.25 | 10.5 | 259.4 | Yes |  |  |  |  | PN12 | 0.2 | 0.1017 | 9
UPVC | PN8 | 300 | 0.3 | UPVC / PN8 / 0.3 | 11.7 | 292 | Yes |  |  |  |  | PN12.5 | 0.25 | 0.1042 | 12
UPVC | PN8 | 375 | 0.375 | UPVC / PN8 / 0.375 | 14.9 | 370.7 | Yes |  |  |  |  | PN15 | 0.3 | 0.1046 | 12.5
UPVC | PN9 | 100 | 0.1 | UPVC / PN9 / 0.1 | 5.55 | 103.15 | Yes | Update!! |  |  |  | PN16 | 0.375 | 0.1061 | 15
UPVC | PN9 | 150 | 0.15 | UPVC / PN9 / 0.15 | 7.75 | 144.8 | Yes | [6 empty] | 0.108 | 16
UPVC | PN9 | 200 | 0.2 | UPVC / PN9 / 0.2 | 9.75 | 205.8 | Yes | [6 empty] | 0.1249 | 18
UPVC | PN9 | 250 | 0.25 | UPVC / PN9 / 0.25 | 12.1 | 256.15 | Yes | [6 empty] | 0.1284 | 20
UPVC | PN9 | 300 | 0.3 | UPVC / PN9 / 0.3 | 13.6 | 288.25 | Yes | [6 empty] | 0.1427 | 25
UPVC | PN9 | 375 | 0.375 | UPVC / PN9 / 0.375 | 17.25 | 367 | Yes | [6 empty] | 0.1462
UPVC | PN12 | 100 | 0.1 | UPVC / PN12 / 0.1 | 6.3 | 101.7 | Yes | [6 empty] | 0.1469
UPVC | PN12 | 150 | 0.15 | UPVC / PN12 / 0.15 | 8.8 | 142.7 | Yes | [6 empty] | 0.1489
UPVC | PN12 | 200 | 0.2 | UPVC / PN12 / 0.2 | 11.1 | 203.1 | Yes | [6 empty] | 0.1517
UPVC | PN12 | 250 | 0.25 | UPVC / PN12 / 0.25 | 13.7 | 252.9 | Yes | [6 empty] | 0.2031
UPVC | PN12 | 300 | 0.3 | UPVC / PN12 / 0.3 | 15.5 | 284.5 | Yes | [6 empty] | 0.2055
UPVC | PN12 | 375 | 0.375 | UPVC / PN12 / 0.375 | 19.6 | 363.3 | Yes | [6 empty] | 0.2085
MPVC | PN9 | 100 | 0.1 | MPVC / PN9 / 0.1 | 3.2 | 108 | Yes | [6 empty] | 0.2093
MPVC | PN9 | 150 | 0.15 | MPVC / PN9 / 0.15 | 4.3 | 151.7 | Yes | [6 empty] | 0.2131
MPVC | PN9 | 200 | 0.2 | MPVC / PN9 / 0.2 | 6.1 | 213.1 | Yes | [6 empty] | 0.2258
MPVC | PN9 | 250 | 0.25 | MPVC / PN9 / 0.25 | 7.5 | 265.5 | Yes | [6 empty] | 0.2286
MPVC | PN9 | 300 | 0.3 | MPVC / PN9 / 0.3 | 8.4 | 298.7 | Yes | [6 empty] | 0.2317
MPVC | PN9 | 375 | 0.375 | MPVC / PN9 / 0.375 | 10.6 | 379.3 | Yes | [6 empty] | 0.2328
MPVC | PN12 | 100 | 0.1 | MPVC / PN12 / 0.1 | 4.1 | 106.1 | Yes | [6 empty] | 0.237
MPVC | PN12 | 150 | 0.15 | MPVC / PN12 / 0.15 | 5.7 | 148.9 | Yes | [6 empty] | 0.2529
MPVC | PN12 | 200 | 0.2 | MPVC / PN12 / 0.2 | 8 | 209.3 | Yes | [6 empty] | 0.2556
MPVC | PN12 | 250 | 0.25 | MPVC / PN12 / 0.25 | 9.9 | 260.6 | Yes | [6 empty] | 0.2594
MPVC | PN12 | 300 | 0.3 | MPVC / PN12 / 0.3 | 11.2 | 293.2 | Yes | [6 empty] | 0.2606
MPVC | PN12 | 375 | 0.375 | MPVC / PN12 / 0.375 | 14.1 | 372.3 | Yes | [6 empty] | 0.2655
MPVC | PN15 | 100 | 0.1 | MPVC / PN15 / 0.1 | 5.1 | 104.2 | Yes | [6 empty] | 0.2845
MPVC | PN15 | 150 | 0.15 | MPVC / PN15 / 0.15 | 7.1 | 146.2 | Yes | [6 empty] | 0.288
MPVC | PN15 | 200 | 0.2 | MPVC / PN15 / 0.2 | 9.9 | 205.5 | Yes | [6 empty] | 0.292
MPVC | PN15 | 250 | 0.25 | MPVC / PN15 / 0.25 | 12.4 | 255.6 | Yes | [6 empty] | 0.2932
MPVC | PN15 | 300 | 0.3 | MPVC / PN15 / 0.3 | 13.8 | 288 | Yes | [6 empty] | 0.2987
MPVC | PN15 | 375 | 0.375 | MPVC / PN15 / 0.375 | 17.5 | 365.6 | Yes | [6 empty] | 0.3633
0.3656
0.3707
0.3723
0.3793
0.4643
0.4729
0.52
0.5296
0.585
0.596