## TS7.2 Disinfection Mixture
TS7.2 Disinfection Mixture
Date of Test: |  | Resource Consent / TCC Contract No.
Development Name and Stage / TCC Contract Name
Project/ Pipe Location
Contractors Reps Name |  | Contractors Company
Certifying Engineers Name |  | Engineers Company
Council Witness Name |  | Council
Guideline Tables
Chlorine Table to achieve 15mg/l
15 |  | 5 | 12 | 15
Pipe Diameter (mm) | Volume of water per 1m length of pipe (l) | Volume of 5% Sodium Hypochlorite (ml) | Volume of 12% Sodium Hypochlorite (ml) | Volume of 15% Sodium Hypochlorite (ml)
50 | 1.9635 | 0.58905 | 0.24544 | 0.19635
100 | 7.854 | 2.3562 | 0.98175 | 0.7854
150 | 17.6715 | 5.3014 | 2.2089 | 1.7671
200 | 31.4159 | 9.4248 | 3.927 | 3.1416
250 | 49.0874 | 14.7262 | 6.1359 | 4.9087
300 | 70.6858 | 21.2058 | 8.8357 | 7.0686
375 | 110.4466 | 33.134 | 13.8058 | 11.0447
400 | 125.6637 | 37.6991 | 15.708 | 12.5664
Chlorine Table to achieve 25mg/l
25 |  | 5 | 12 | 15
Pipe Diameter (mm) | Volume of water per 1m length of pipe (l) | Volume of 5% Sodium Hypochlorite (ml) | Volume of 12% Sodium Hypochlorite (ml) | Volume of 15% Sodium Hypochlorite (ml)
50 | 1.9635 | 0.98175 | 0.40906 | 0.32725
100 | 7.854 | 3.927 | 1.6362 | 1.309
150 | 17.6715 | 8.8357 | 3.6816 | 2.9452
200 | 31.4159 | 15.708 | 6.545 | 5.236
250 | 49.0874 | 24.5437 | 10.2265 | 8.1812
300 | 70.6858 | 35.3429 | 14.7262 | 11.781
375 | 110.4466 | 55.2233 | 23.0097 | 18.4078
400 | 125.6637 | 62.8319 | 26.1799 | 20.944 | Example:
Pipe Disinfection - Inputs
Required Hypochlorite Dose Rate (mg/l) (ppm) |  |  |  | mg/l | 25 | mg/l
% Hypochlorite (NaOCl) solution to be used |  |  |  | % | 15 | %
Pipe Size (Internal Diameter) |  |  |  | mm | 50 | mm
Pipe Length |  |  |  | m | 162 | m
Pipe Disinfection - Calculations
Pipe Volume π x (Pipe Size (mm) / 2000)2 x Length (m) |  |  |  | m3 | 0.31809 | m3
Amount of Hypochlorite needed - kg Pipe Volume (m3) x Dose Rate (mg/l) / (Hypo solution (%) x 10) |  |  |  | kg | 0.053014 | kg
Amount of Hypochlorite needed - litres Hypochlorite (kg) / 1.2 |  |  |  | l | 0.044179 | l
Water per litre Hypochlorite needed Pipe Volume (m3) / Hypochlorite (litres) x 1000 |  |  |  | l | 7200 | l
Test Certification
I certify that this test was undertaken to the requirements of the Infrastructure Development Code
…………………………..……………………. | (Contractor's Representative) |  | …………………………..……………………. | (Certifying Engineer)
I certify that I was in attendance during the testing procedure acting as a witness for Tauranga City Council
…………………………..……………………. | (Council's Representative)

## TS7.3 De-chlorination Mixture
TS7.3 De-chlorination Mixture
Date of Test |  | Resource Consent / TCC Contract No.
Development Name and Stage / TCC Contract Name
Project/ Pipe Location
Contractors Rep's Name |  | Contractor's Company
Certifying Engineer's Name |  | Engineer' Company
Council Witness Name |  | Council |  |  | Example:
De-Chlorination (Sodium Thiosulphate) Calculator to de-chlorinate a volume of water
Volume of Pipe |  |  | m3 |  | 25.8 | m3
Measured Free Available Chlorine (FAC) |  |  | mg/l |  | 10 | mg/l
Desired FAC |  |  | mg/l | Factor | 0.05 | mg/l
FAC to remove (Measured FAC - Desired FAC) |  | 0 | g/m3 | 1.86 | 9.95 | g/m3
Chlorine to Remove FAC to remove x pipe volume (m3) / 1000 |  | 0 | Kg Cl2 | @ pH 8 | 0.25671 | Kg Cl2
Thiosulphate needed (at pH8 with factor 1.86) Chlorine to Remove (kg) x 1.86 |  | 0 | kg |  | 0.47748 | kg
De-Chlorination Guideline for other De-Chlorination chemicals
Table Showing Amount of Chemical to make up 15% w/v Solution
Solution Volume (litres) | Sodium Thiosulphite (kg) | Anhydrous Sodium Sulphite (kg) | Sulphite Heptahydrate (kg)
100 | 15.2 | 15 | 30
200 | 30.3 | 30 | 60
300 | 45.5 | 45 | 90
400 | 61 | 60 | 120
500 | 76 | 75 | 150
600 | 91.3 | 90 | 180
700 | 106.2 | 105 | 210
800 | 121.2 | 120 | 240
900 | 136 | 135 | 270
1000 | 151.5 | 150 | 300 |  | Example:
De-Chlorination calculation to de-chlorinate a flow of super chlorinated water
FAC of Water e.g. 20.0 |  |  | mg/l |  | 20 | mg/l
Flow of Water to be dechlorinated e.g. 100 |  |  | L/min |  | 100 | L/min
Dechlorination Solution Strength (see table above to achieve this) e.g. 15 |  |  | % |  | 15 | %
Litres of Solution - FAC of Water (mg/l) x 3 x Flow of water (l/min) / solution strength (%) / 10000 (x 60 for l/hr) |  |  | L/min |  | 0.04 | L/min
|  |  | L/hr |  | 2.4 | L/hr
Test Certification
I certify that this test was undertaken to the requirements of the Infrastructure Development Code
……………………………………………………………. | (Contractor's Representative) | …………………………………………………………. | (Certifying Engineer)
I certify that I was in attendance during the testing procedure acting as a witness for Tauranga City Council
…………………………………………………………….. | (Council's Representative)